Model  List:     T66-CC-30W-1200K-40H

Report Type:     According to the TM - 21 lamp bead LM80 report, formula L90B10,L90B20 ,L90B50 life of lamps and lanterns

Test Engineer:    Chris Xie

Report Number： ERVAN-2022102101

Report Date：    2022-10-21

- General Description

Information of Final Products:

| Model Name: | LED Tri-proof Light |
| --- | --- |
| Manufacturer: | Shenzhen Ruizi Light Electricity Technology Co.,Ltd. |
| Brand Name: | ERVAN |

Information of LED Light Source:

Model Number of LED Light Source:       2835 White SMD LED

Manufacturer:       JuFei Corporation

LM80 Report:      R2DG160507060-10-10000

Formula is derived:      TM-21

Drive Current:      57mA

The applied current:      60mA

LED temperature:      57.2°C

The environment temperature：     25℃

Collect the number:      20

|  | L90 |
| --- | --- |
| 1 | 55000 |
| 2 | 56000 |
| 3 | 48000 |
| 4 | 67000 |
| 5 | 58000 |
| 6 | 61000 |
| 7 | 70000 |
| 8 | 51000 |
| 9 | 62000 |
| 10 | 59000 |
| 11 | 50000 |
| 12 | 58000 |
| 13 | 49000 |
| 14 | 50000 |
| 15 | 45000 |
| 16 | 52000 |
| 17 | 76000 |
| 18 | 55000 |
| 19 | 59000 |
| 20 | 69000 |
| L90B10 | 49000 |
| L90B20 | 50000 |
| L90B50 | 56000 |